## Sheet 1
Water Source Heat Pump
KHPR280
Unit Info
Project: | Air Cooled Condenser First Project | Revision: |  | R0
Customer: | TMU | Location:
Unit Tag: |  | Prepared By:
Date: | 05/05/2026 |  | Qty: | 1
Tracking No:
Overall Performance
Total Cooling Capacity | 288.58 MBH |  | Total Heating Capacity |  | 372.08 MBH
Sensible Capacity | 199.82 MBH |  | Total Power Input (KW) |  | 31.89
| Air Flow | 8,486 CFM | Altitude |  | 0 ft
External Static Pressure |  | 1.00 inWG | Refrigerant |  | R454B
Unit Electrical Data
Power supply | 460/3/60 |  | MOP |  | 60
MCA | 46
Filter Details
Filter Class | MERV 8, Synthetic type | Filter holding frame |  |  | Expanded metal grid
Face velocity | 364 ft/min
Supply Fan
Fan Model | ATLI1515BT | Motor Power |  |  | 4.14
Fan Type | Forward | Power Supply |  |  | 460 / 3 / 60
Drive Type |  |  | Motor Qty |  | 1
Fan Qty |  | 1 | Motor FLA |  | 10.7
Heat Exchanger Data
Fin Tube Type :
Coil Area | 23.33 ft² | Face Velocity |  |  | 363.7ft/min
Tube Material | Copper |  | Tube Dia |  | 3/8
Fin Material | Aluminum | Fin Thickness |  |  | 0.006 inch
Plate Heat Exchanger :
Connection Size |  |  | Qty |  | 2
Connection Type | FPT
Condensate Drain :
Connection Size
Cooling Performance
Inlet DB Temp | 80.0 °F | Outlet DB Temp |  |  | 58.2 °F
Inlet WB Temp | 67.0 °F | Outlet WB Temp |  |  | 56.0 °F
Air Side Pressure Drop | 2.08 inWG | Refrigerant Pressure Drop |  |  | 2.01 PSI
Inlet Water Temp | 86.0 °F | Leaving Water Temp |  |  | 95.9 °F
Water Flow Rate | 35.00000 US gpm | Water Pressure Drop |  |  | 38.70 kPa
CONTINUING RESEARCH RESULTS IN STEADY IMPROVEMENTS. THEREFORE, UNIT DIMENSIONS AND SPECIFICATIONS ARE SUBJECTED TO CHANGE WITHOUT NOTICE
1.0.0.179
www.3esol.com
www.thermoplus.com
1 of 4

## Sheet 2
Water Source Heat Pump
KHPR280
Unit Info
Project: | Air Cooled Condenser First Project | Revision: | R0
Customer: | TMU | Location:
Unit Tag: | Prepared By:
Date: | 05/05/2026 | Qty: | 1
Tracking No:
Heating Performance
Inlet DB Temp | 47.0 °F | Outlet DB Temp |  | 85.6 °F
Inlet WB Temp | 43.0 °F Outlet WB Temp |  |  | 59.7 °F
Air Side Pressure Drop | 2.08 inWG Refrigerant Pressure Drop |  |  | 0.99 PSI
Inlet Water Temp | 68.0 °F Leaving Water Temp |  |  | 60.2 °F
Water Flow Rate | 35.00000 US gpm Water Pressure Drop |  |  | 57.86 kPa
Compressor
Type | Hermetically sealed Scroll | Current (LRA ) |  | 140
Brand | Copeland | Qty |  | 2
Power Supply | 460/3/60 | Power input |  | 16.5
Current (RLA ) | 15.4 | Refrigerant |  | R454B
Optional Features
Expansion Valve | 1
Fan Performance
1.0.0.179
www.3esol.com
www.thermoplus.com
2 of 4

## Sheet 3
Water Source Heat Pump
KHPR280
Unit Info
Project: | Air Cooled Condenser First Project | Revision: | R0
Customer: | TMU | Location:
Unit Tag: |  | Prepared By:
Date: | 05/05/2026 | Qty: | 1
Tracking No:
PS Chart
PH Diagram
1.0.0.179
www.3esol.com
www.thermoplus.com
3 of 4

## Sheet 4
Water Source Heat Pump
KHPR280
Unit Info
Project: | Air Cooled Condenser First Project | Revision: | R0
Customer: | TMU | Location:
Unit Tag: |  | Prepared By:
Date: | 05/05/2026 | Qty: | 1
Tracking No:
1.0.0.179
www.3esol.com
www.thermoplus.com
4 of 4