1 of 4

1.0.0.179 www.3esol.com

www.thermoplus.com

CONTINUING RESEARCH RESULTS IN STEADY IMPROVEMENTS. THEREFORE, UNIT DIMENSIONS AND SPECIFICATIONS ARE SUBJECTED TO CHANGE WITHOUT NOTICE

Cooling Performance

Condensate Drain :

Plate Heat Exchanger :

Fin Tube Type :

Heat Exchanger Data

Supply Fan

Filter Details

Unit Electrical Data

R454B

0 ft

Refrigerant

31.89

Altitude

372.08 MBH

Total Power Input (KW)

Total Heating Capacity

Overall Performance

1

R0

Revision:

Location:

Prepared By:

Qty:

05/05/2026

Air Cooled Condenser First Project TMU

Project:

Customer:

Unit Tag:

Date:

Tracking No:

Unit Info

KHPR280

Water Source Heat Pump

| Total Cooling Capacity | 288.58 MBH |
| --- | --- |
| Sensible Capacity | 199.82 MBH |
| Air Flow | 8,486 CFM |
| External Static Pressure | 1.00 inWG |

| Power supply | 460/3/60 | MOP | 60 |
| --- | --- | --- | --- |
| MCA | 46 |  |  |

| Filter Class | MERV 8, Synthetic type | Filter holding frame | Expanded metal grid |
| --- | --- | --- | --- |
| Face velocity | 364 ft/min |  |  |

| Fan Model | ATLI1515BT | Motor Power | 4.14 |
| --- | --- | --- | --- |
| Fan Type | Forward | Power Supply | 460 / 3 / 60 |
| Drive Type |  | Motor Qty | 1 |
| Fan Qty | 1 | Motor FLA | 10.7 |

| Coil Area | 23.33 ft² | Face Velocity | 363.7ft/min |
| --- | --- | --- | --- |
| Tube Material | Copper | Tube Dia | 3/8 |
| Fin Material | Aluminum | Fin Thickness | 0.006 inch |

| Connection Size |  | Qty | 2.00 |
| --- | --- | --- | --- |
| Connection Type | FPT |  |  |

| Connection Size |  |
| --- | --- |

| Inlet DB Temp | 80.0 °F | Outlet DB Temp | 58.2 °F |
| --- | --- | --- | --- |
| Inlet WB Temp | 67.0 °F | Outlet WB Temp | 56.0 °F |
| Air Side Pressure Drop | 2.08 inWG | Refrigerant Pressure Drop | 2.01 PSI |
| Inlet Water Temp | 86.0 °F | Leaving Water Temp | 95.9 °F |
| Water Flow Rate | 35.00000 US gpm | Water Pressure Drop | 38.70 kPa |

1

R0

Revision:

Location:

Prepared By:

Qty:

05/05/2026

Air Cooled Condenser First Project TMU

Project:

Customer:

Unit Tag:

Date:

Tracking No:

Unit Info

KHPR280

Water Source Heat Pump

Heating Performance

| Inlet DB Temp | 47.0 °F | Outlet DB Temp | 85.6 °F |
| --- | --- | --- | --- |
| Inlet WB Temp | 43.0 °F | Outlet WB Temp | 59.7 °F |
| Air Side Pressure Drop | 2.08 inWG | Refrigerant Pressure Drop | 0.99 PSI |
| Inlet Water Temp | 68.0 °F | Leaving Water Temp | 60.2 °F |
| Water Flow Rate | 35.00000 US gpm | Water Pressure Drop | 57.86 kPa |

Compressor

| Type | Hermetically sealed Scroll | Current (LRA ) | 140.0 |
| --- | --- | --- | --- |
| Brand | Copeland | Qty | 2 |
| Power Supply | 460/3/60 | Power input | 16.50 |
| Current (RLA ) | 15.4 | Refrigerant | R454B |

Optional Features

| Expansion Valve | 1 |
| --- | --- |

Fan Performance

1.0.0.179

www.3esol.com

www.thermoplus.com

2 of 4

1

R0

Revision:

Location:

Prepared By:

Qty:

05/05/2026

Air Cooled Condenser First Project TMU

Project:

Customer:

Unit Tag:

Date:

Tracking No:

Unit Info

KHPR280

Water Source Heat Pump

PS Chart

PH Diagram

1.0.0.179

www.3esol.com

www.thermoplus.com

3 of 4

Water Source Heat Pump

KHPR280

Unit Info

Project:

Customer:

Unit Tag:

Date:

Tracking No:

Air Cooled Condenser First Project TMU

05/05/2026

Revision:

Location:

Prepared By:

Qty:

R0

1

1.0.0.179 www.3esol.com

www.thermoplus.com

4 of 4